## Sheet1
pos./r.br. | ITEM DESCRIPTION / OPIS | [5 empty] | COUNTING / PREDRAČUN
| NAME |  |  |  | DESCRIPTION |  | UOM / JM | quantity / količina | unt/kom. Price | AMOUNT
1 |  | 参考图片 |  | 贵司提供图片
2 | Light Fixtures 2x49W T5 fluorescent lamps |  |  |  | Supply and installation of recessed light fixtures with pressed-steel back-box; anodized, extruded aluminium mounting frame/trim; flat diffuser of reflecting prismatic polycarbonate; polyester-based, UV-proof, white epoxy powder coat finish for clean rooms; protection class IP40, complete with two 49W T5 fluorescent lamps; equipped with electronic wiring and thermal overload relay; fittings and accessories included. | 嵌入式灯盘，挤压铝边框，菱晶型面板，2x49W T5, IP40 | unt/kom. | 121 |  | 0
3 | Light Fixtures 1x18W fluorescent lamp |  |  |  | Supply and installation of ceiling light fixtures with extruded aluminium housing; die-cast aluminium end plates and one 18W lamp; antiglare, smooth Plexiglas diffuser; high-performance, glazed aluminium reflector with electronic wiring. | 挤压铝灯身，压铸铝尾盖，1x18W,防眩光平滑面罩 | unt/kom. | 3163 |  | 0
4 | Light Fixtures 1x18W fluorescent lamp with pictogram |  |  |  | Supply and installation of ceiling light fixtures with extruded aluminium housing; die-cast aluminium end plates and one 18W lamp; antiglare, smooth Plexiglas diffuser; high-performance, glazed aluminium reflector with electronic wiring. With pictogram. | 挤压铝灯身，压铸铝尾盖，1x18W, 防眩光平滑面罩，带指示标志 （应该是紧急出口之类的标志） | unt/kom. | 169 |  | 0
#REF! | Light Fixtures 2x28W fluorescent lamp: IP65 |  | 镀锌钢底座 |  | Supply and installation of polycarbonate ceiling luminaries with two 28W lamps; injection-moulded, prismatic, clear polycarbonate diffuser; galvanized-steel, UV-proof reflector, pre-painted and with a polyester resin coat finish; electronic wiring to EEI A2; protection class IP65. Turn-key fittings and accessories included. | 2x28W 灯具，注塑模，棱晶型清光PC罩，镀锌钢底座，防UV，IP65 | unt/kom. | 628 |  | 0
#REF! | Light Fixtures 3x14W T5 fluorescent lamps: Dark light optics |  |  |  | Supply and installation of recessed light fixtures with double parabolic louver (dark-light optics); antireflective (99.99 reflectivity), anti-iridescence and low-luminance mirror-aluminium reflector; anionic electrocoat finish, white, UV-proof; complete with three 14W T5 fluorescent lamps; equipped with electronic wiring and thermal overload relay; fittings and accessories included. | 3x14w T5荧光灯嵌入式灯盘，双抛物线百叶 铝反射器（暗灯光学）；铝反射率99.99，抗晕和低亮度镜面铝反射器；电泳表面，边框白色，防UV；配有电子线路和热过载继电器 | unt/kom. | 2912 |  | 0
#REF! | Light Fixtures 4x14W T5 fluorescent lamps: Dark light optics |  |  |  | Supply and installation of recessed light fixtures with double parabolic louver (dark-light optics); antireflective (99.99 reflectivity), anti-iridescence and low-luminance mirror-aluminium reflector; anionic electrocoat finish, white, UV-proof; complete with four 14W T5 fluorescent lamps; equipped with electronic wiring and thermal overload relay; fittings and accessories included. | 4x14w T5荧光灯嵌入式灯盘，双抛物线百叶 铝反射器（暗灯光学）；铝反射率99.99，抗晕和低亮度镜面铝反射器；电泳表面，边框白色，防UV；配有电子线路和热过载继电器 | unt/kom. | 1279 |  | 0
#REF! | Light Fixtures 4x14W T5 fluorescent lamps, IP54 for clean room |  | IP54 |  | Supply and installation of recessed light fixtures with pressed-steel back-box; anodized, extruded aluminium mounting frame/trim; flat diffuser of reflecting prismatic polycarbonate; polyester-based, UV-proof, white epoxy powder coat finish for clean rooms; protection class IP54, complete with four 14W T5 fluorescent lamps; equipped with electronic wiring and thermal overload relay; fittings and accessories included. | 4x14W 嵌入式洁净灯具；阳极氧化，白色喷粉挤压铝安装边框；棱镜PC罩、防紫外；防护等级IP54，配有电子线路和热过载继电器配件。 | unt/kom. | 1442 |  | 0
#REF! | Light Fixtures 4x18W fluorescent lamp: IP40 for clean rooms |  | IP40 |  | Supply and installation of recessed light fixtures with pressed-steel back-box; anodized, extruded aluminium mounting frame/trim; flat diffuser of reflecting prismatic polycarbonate; polyester-based, UV-proof, white epoxy powder coat finish for clean rooms; protection class IP40, complete with four 18W T5 fluorescent lamps; equipped with electronic wiring and thermal overload relay; fittings and accessories included. | 4x14W 嵌入式洁净灯具；阳极氧化，白色喷粉挤压铝安装边框；棱镜PC罩、防紫外；防护等级IP40，配有电子线路和热过载继电器配件。 | unt/kom. | 1473 |  | 0
#REF! | Light Fixtures 2x14W fluorescent lamp: IP65 |  |  |  | Supply and installation of polycarbonate ceiling luminaries with two 14W lamps; injection-moulded, prismatic, clear polycarbonate diffuser; galvanized-steel, UV-proof reflector, pre-painted and with a polyester resin coat finish; electronic wiring to EEI A2; protection class IP65. Turn-key fittings and accessories included. | 2x14W 灯具，注塑模，棱晶型清光PC罩，镀锌钢底座，防UV，IP65 | unt/kom. | 10 |  | 0
#REF! | Light Fixtures 4x14W T5 fluorescent lamps: IP65 for clean rooms |  | 洁净灯盘 |  | Supply and installation of recessed light fixtures with double parabolic louver; antireflective (99.99 reflectivity), anti-iridescence and low-luminance mirror-aluminium reflector; with pressed-steel back-box; anodized, extruded aluminium mounting frame/trim; 4 mm thick tempered glass, "Ice Crystal” pattern or opal polycarbonate flat diffuser; polyester-based, UV-proof, white epoxy powder coat finish for clean rooms; protection class IP65, complete with four 14W T5 fluorescent lamps; equipped with electronic wiring and thermal overload relay; fittings and accessories included. | 4x14W嵌入式洁净灯具；双抛物线百叶反射（反射率99.99），抗晕和低亮度镜面铝；挤压铝边框；4毫米厚的钢化玻璃，防紫外、白色喷粉涂层；防护等级IP65；配有电子线路和热过载继电器。 | unt/kom. | 929 |  | 0
#REF! | Light Fixtures 4x54W T5 fluorescent lamps: IP65 for clean rooms |  | 洁净灯盘 |  | Supply and installation of recessed light fixtures with double parabolic louver; antireflective (99.99 reflectivity), anti-iridescence and low-luminance mirror-aluminium reflector; with pressed-steel back-box; anodized, extruded aluminium mounting frame/trim; 4 mm thick tempered glass, "Ice Crystal” pattern or opal polycarbonate flat diffuser; polyester-based, UV-proof, white epoxy powder coat finish for clean rooms; protection class IP65, complete with four 54W T5 fluorescent lamps; equipped with electronic wiring and thermal overload relay; fittings and accessories included. | 4x54W嵌入式洁净灯具；双抛物线百叶反射（反射率99.99），抗晕和低亮度镜面铝；挤压铝边框；4毫米厚的钢化玻璃，防紫外、白色喷粉涂层；防护等级IP65；配有电子线路和热过载继电器。 | unt/kom. | 246 |  | 0
#REF! | Lighting equipment for bedhead unt/kom. |  |  |  | Supply and installation of two 36W lamps, 1+1 18W direct light services, two push-buttons and one switch for a bedhead unt/kom. with beam carrier of extruded aluminium and rounded edges, white paint withstanding any disinfectant or cleaner. The beam is made up of three separate compartments: upper channel section with two 36W lamps for indirect lighting; middle channel section with 1+1 18W direct light services, three UNEL electrical sockets 10/16A+E, two relays, one 230/24 V transformer, two push-buttons, one switch, two RJ45 sockets to Class 6, and keyboard for nurse call system; lower channel section reserved to medical gas distribution. Downlight of highly reflective aluminium for indirect lighting. Lower diffuser of reinforced, antiglare, injection-moulded clear polycarbonate. Upper diffuser of injection-moulded clear polycarbonate. Low-loss starter wiring to EEI B2. Turn-key fittings and accessories included. | 床头照明系统： 2x36w灯具间接照明 以及1+1 18W直接照明。带有挤压铝和圆形边缘边框，白色表面处理能承受任何消毒剂或清洁剂。 光源有三个独立的部分：两边的2x36W 提供间接照明；中间部分提供 1+1 18w直接照明，3个UNEL插座10 / 16a E，两个继电器，一个230 / 24 V变压器，两个按钮，一个开关，两个RJ45插座6类，和键盘的护士呼叫系统；低槽段保留医疗气体分布。铝反射罩的筒灯或者射灯起间接照明作用。上下两端有注塑成型的防炫光清光PC罩。低损耗起动器接线EEI B2。 | unt/kom. | 1042 |  | 0
#REF! | Light Fixtures 1x18W fluorescent lamp, emegency outlet, with pictogram |  | 带3小时应急 |  | Supply and installation of ceiling light fixtures with polycarbonated housing and one 18W lamp; emergency outlet; antiglare, smooth Plexiglas diffuser; high-performance, glazed aluminium reflector with electronic wiring. With pictogram. Emergency run time: 180 minutes. When power is restored, the battery recharges automatically in 12 hours. | 1x18W PC底座吸顶灯，有应急装置，光滑pc透光罩， 铝反射罩。应急时间： 180分钟，电力接通后电池在12小时内自动充电。 | unt/kom. | 339 |  | 0
#REF! | Luminaries for on-wall or ceiling mounting IP65 2x28W Fluorescent lamps |  |  |  | Supply of the attachable for on-wall or ceiling mounting, with polycarbonate diffuser 2x28W. Protection IP65. Complete light fitting with mounting attachments | 墙面或者吸顶安装灯具， 2x28W， PC透光罩，IP65 | unt/kom. | 441 |  | 0
#REF! | Light Fixtures 1x8W compact fluorescent lamp |  |  |  | Supply and installation of ceiling light fixtures with extruded aluminium housing; die-cast aluminium end plates and one 8W lamp; antiglare, smooth Plexiglas diffuser; high-performance, glazed aluminium reflector with electronic wiring. | 挤压铝灯身，压铸铝尾盖，1x8W,防眩光平滑面罩 | unt/kom. | 339 |  | 0
#REF! | Lighting luminare IP65 2x14W |  |  |  | Lighting luminare IP65 with T5 fluorescent lamp 2x14w | T5 2x14W IP 65 灯具 （说的太泛，应该是三防支架灯？） | unt/kom. | 12 |  | 0
#REF! | Light Fixtures 1x18W fluorescent lamp |  |  |  | Supply and installation of ceiling light fixtures with polycarbonated housing and one 18W lamp; emergency outlet; antiglare, smooth Plexiglas diffuser; high-performance, glazed aluminium reflector with electronic wiring. | 1x18W PC底座吸顶灯，有应急装置，光滑pc透光罩， 铝反射罩。 | unt/kom. | 37 |  | 0
#REF! | light low intensity red led IP55 |  |  |  | Obstacle light low intensity, omndirectional, fixed red led icao type B with two different bulb light IP55 | 避光强度低，全向，固定的红色LED，国际民航组织B型，两种不同的灯泡，IP55 | unt/kom. | 6 |  | 0